## Slide 1
2. Aim
We evaluated HEPA-based stand-alone air decontamination systems, which offer the potential to reduce risk associated with contaminated air in hospitals, especially where ventilation is inadequate.
3. Methods
A structured evaluation of the technical specification of HEPA-based air disinfection systems currently available on the UK market allowed us to select four units that had sufficient manufacturer-claimed airflow rate to achieve a theoretical 6 air purifications per hour in a typical single room. The units were tested to measure airflow rate, noise level, the ability to remove smoke released at various points in the room, the impact on particle counts, and a structured engineering review of the unit to include ease of use and maintenance. Active microbiological air sampling was undertaken. Testing was undertaken in a single hospital room with a volume of 38m3.
4. Results
Preliminary testing was undertaken to optimise the room location of the systems. Particle count testing showed that the higher the setting, the more impact on particles that could be identified in the room (Table 1). All units had variable speed settings. The noise level varied from 34 to 71 dBA. Noise levels and airflows were consistent with manufacturer claims (Tables 2 and 3). Smoke testing showed the units were able to pull in air from most parts of the room. Microbial counts in the air before the units were activated were very low, meaning that the impact on the units in reducing microbial contamination could not be measured. The engineering review concluded that all units are relatively low-maintenance.
5. Conclusion
Our technical specification review narrowed down the wide range of options to those systems that are likely to deliver a meaningful improvement in air quality in hospital rooms. Comparative evaluation of the devices using standardised methods provides useful data to inform decisions about unit selection. The noise levels that we measured were higher than permitted noise levels in hospital wards (35 dBA, HTM-03). Further testing is planned to include more units in a range of room sizes and microbiological air sampling.
Comparative evaluation of stand-alone HEPA-based air decontamination systems
Jonathan A. Otter (jon.otter@gstt.nhs.uk),1 Louise Clark, 2 Graham Taylor, 3
Amal Hussein, 1 Latchmin Gargee, 1 Simon D. Goldenberg1
1. Directorate of Infection, Guy’s and St. Thomas NHS Foundation Trust (GSTT)
2. Department of Engineering, Essentia, GSTT
3. Authorising Engineer, GPT Consult LLP
Conflict of interest: JO consults for Gama Healthcare.
1. Introduction
Contaminated air can be a vector for the transmission of key hospital pathogens, including respiratory viruses such as SARS-CoV-2. Ventilation in healthcare buildings frequently falls below minimum standards. Key pathogens can be identified in hospital air, in a range of particle sizes (e.g. Influenza, MERS, and SARS (including COVID-19)).1,2 Also, pathogens not traditionally associated with contamination of the air can be found in the air (e.g. C. difficile, Acinetobacter and MRSA).3-4 The latest UK hospital guidance for SARS-CoV-2 and other respiratory viruses includes a recommendation to consider alternative technologies to improve air hygiene when ventilation is considered inadequate or cannot be assessed.
1. Otter et al. J Hosp Infect 2016; 92: 235-50.
2. Bischoff et al. J Infect Dis 2013; 207: 1037-46.
3. Munoz-Price et al. Crit Care Med 2013; 41: 1915-8.
4. Best et al. Clin Infect Dis 2010; 50: 1450-7.
 | Unit A (Rediair) | Unit B (Rensair) | Unit C (CamFil) | Unit D (Air Sentry)
Airflow m3/hr | Up to 600 | 300-560 | 37-433 | 1960
Noise dBA | 22-66 | 45-59 | 16-54 | 58
Weight | 14 kg | 18 kg | 15 kg | 25 kg
Size HxWxD cm | 40x40x67 | 84x43x43 | 72x34x35 | 105x39x59
HEPA | H14 | H13 | H14 | H14
Power usage W | 90 | 160-220 | 4-55 | 30-150
Table 2: Comparison of specification
Table 2: Measurement of noise and airflow
Unit | Unit A (Rediair) |  |  | Unit B (Rensair) |  |  | Unit C (CamFil) |  |  | Unit D (Air Sentry) |  | 
Speed setting | Low | Med | High | Low | Med | High | 1 | 3 | 6 | 1 | 2 | 3
Airflow m3/hr | 317 | 425 | 623 | 277 | 356 | 439 | 29 | 130 | 472 | 405 | 614 | 1228
Noise dBA | 39 | 42 | 50 | 51 | 55 | 61 | 34 | 34 | 56 | 51 | 58 | 71
Table 3: Comparison of measured airflow and noise
 | Unit A (Rediair) |  |  | Unit B (Rensair) |  |  | Unit D (Air Sentry) |  | 
Airflow m3/hr | Off | 622 | % reduction | Off | 356 | % reduction | Off | 1228 | % reduction
0.3 µm | 8912140 | 3589400 | 59.7 | 254304 | 181147 | 28.8 | 4821060 | 896520 | 81.4
0.5 µm | 380460 | 228900 | 39.8 | 133867 | 91097 | 31.9 | 265960 | 41600 | 84.4
1 µm | 28420 | 17680 | 37.8 | 29078 | 19583 | 32.7 | 25720 | 4040 | 84.3
3 µm | 600 | 380 | 36.7 | 4104 | 4451 | -8.5 | 1320 | 400 | 69.7
5 µm | 260 | 180 | 30.8 | 35 | 208 | -494.3 | 540 | 200 | 63.0
Table 1: Impact on particle detected